Kuiper 61” Telescope

UPS Start Up/Shut Down Procedure

John Morris

7/10/24

Start up:

- Plug in the UPS feed cable.

- Turn on the UPS feed breaker.

- Turn on the DC breaker (in the UPS lower panel, use key to open).

- Turn on the UPS key switch and wait for ready light on panel.

- Plug in the UPS output cable.

- Turn on the UPS output breaker.

- It is now safe to plug into clean (orange) power outlets.

Shut down:

- Unplug everything plugged into a clean (orange) power outlet.

- Turn off UPS output breaker.

- Turn UPS key switch off.

- Turn off DC breaker (in the UPS lower panel, use key to open).

- Turn off UPS feed breaker.

- Unplug UPS feed and output cables.

Numbers above reference Start Up steps